## Leak Check ODS
Controlled ozone depleting substances (ODS) subject to the ODS Regulation are listed in Annex I of the ODS Regulation (EC 1005/2009).
General ODS containment requirements: I. Undertakings shall take all precautionary measures practicable to prevent and minimise any leakages and emissions of ODS. II. Undertakings operating refrigeration, air conditioning or heat pump equipment, or fire protection systems, including their circuits, which contain controlled ODS shall ensure that the stationary equipment or system is leak checked by a certified person as a minimum at the mandatory frequencies outlined in table 1 below, which are determined by the refrigerant charge size of the equipment:
Table 1. Mandatory Leak Checking Frequencies
III. Where a leak of ODS is detected, the ODS Regulation requires operators to complete a repair as soon as possible and in any event within 14 days in order to minimise any futher leakage. However, it should be noted that while a unit of equipment which contains an ODS refrigerant can continue to be used after the 1st January 2015, should the unit leak refrigerant, it can no longer be topped up with ODS refrigerants (for example R12 and R22) in order to repair the system. If a leak occurs, the refrigerant gas in the system would either have to be completely replaced with an alternative non-ODS gas (if feasible) or the whole system would have to be replaced with an alternative system. IV. The ODS Regulation require that a repaired leak is checked by a certified person within one month after the repair to ensure that the repair has been effective. However, this recheck can take place on the same day that the leak is fixed after the system has been repaired and is back in balanced operation. V. The operator of equipment containing ODS is required to maintain records for each piece of equipment containing 3kg or more of ODS as specified by Article 23(3) of the ODS Regulations up to and including its decommissioning. It is recommended that these records are maintained for at least 5 years. VI. A certified person for the purpose of undertaking leak checking shall hold an appropriate cetificate. In order to demonstrate compliance with this requirement, it is recommended that a copy of the refrigeration technician's certificate is obtained and retained on file for inspection. A certificate for leak checking F-Gases in similar equipment, such as the QQI (formerly FETAC) F-Gas handling certificate or equivalent, is acceptable.
IMPORTANT: This document does not purport to be and should not be considered a legal interpretation of the legislation referred to herein. Although every effort has been made to ensure the accuracy of the material contained in this document, complete accuracy cannot be guaranteed. Neither the Environmental Protection Agency nor the authors accept any responsibility whatsoever for loss or damage occasioned, or claimed to have been occasioned, in part or in full as a consequence of any person acting or refraining from acting, as a result of a matter contained in this publication.

## Leak Check F-gas
Fluorinated Greenhouse Gases (F-gases) subject to control are listed in Annex I of the F-Gas Regulation (EU 517/2014).
General F-Gas Containment Requirements I. The intentional release of fluorinated greenhouse gases into the atmosphere shall be prohibited where the release is not technically necessary for the intended use. II. Operators of equipment that contains fluorinated greenhouse gases shall take precautions to prevent the unintentional release (‘leakage’) of those gases. They shall take all measures which are technically and economically feasible to minimise leakage of fluorinated greenhouse gases. III. Where a leakage of fluorinated greenhouse gases is detected, the operators shall ensure that the equipment is repaired without undue delay.
Leak Checking Requirements for refrigerant gas I. The threshold for mandatory leak checking is determined by the charge size of the refrigerant expressed in tonnes carbon dioxide equivalent (tCO2eq). The CO2 equivalent of an F-gas is calculated by multiplying the mass in tonnes by the Global Global Warming Potential (GWP) of that particular refrigerant gas. II. Stationary refrigeration, air conditioning and heat pump equipment containing 5 tCO2eq of F-gases or more (10 tCO2eq or more if the refrigerant is hermetically sealed within the equipment) must be checked for refrigerant leakage by certified personnel at the following minimum frequencies oulined in table 1: III. Newly installed equipment should be checked for leakage immediately after they have been put into service.
Leak Checking Requirements for Electrical Switchgear Electrical switchgear is not subject to leak checking provided the equipment complies with the following: a. It has a tested leakage rate of <0.1 % per year as set out in technical specifications and is labelled accordingly, b. It is equipped with a pressure or density monitoring device, or c. It contains less than 6 kg of F-gas. If these exemptions apply, mandatory equipment F-Gas records are not required. However, it is recommended as best practice to maintain records which detail: • the quantity of installed SF6 (i.e. the equipment’s charge of SF6); • monitoring for leakage; • the detection and repair of leaks; • the quantities of SF6 used to top-up equipment; • the decommissioning of equipment and the recovery of SF6, and • the name of the F-Gas certified technician.
Leak checking requirements for Stationary Fire Protection Equipment Leak checking requirements for stationary fire protection equipment shall be considered to be fulfilled provided the following two conditions are met: a. The inspection regime meets ISO 14520 or EN 15004 (related to design and properties of fire extinguishing systems), and b. The fire protection equipment is inspected in accordance with the frequencies outlined in Table 1. above.
Requirements for Automatic Leak Detection Systems There are two criteria in the EU F-Gas Regulation for the mandatory installation of an automated leak detection system outlined below: I. CO2 eq: Operators of stationary refrigeration, air conditioning, heat pump and fire protection equipment containing 500 tCO2eq of F-gases or more shall ensure that the equipment is provided with a leak detection system which alerts the operator or a service company of any leakage. Leak detection systems must be checked at least once every 12 months to ensure their proper functioning and records of this should be maintained for at least 5 years. II. SF6: Operators of electrical switchgear and organic rankine cycles containing SF6 in quantities of 500 tCO2eq or more and installed from 1 January 2017 shall ensure that this equipment is provided with a leak detection system which alerts the operator or a service company of any leakage. Leak detection systems must be checked at least once every 6 years to ensure their proper functioning and it is recommended that records of this should be maintained for at least 5 years.
Leakage Detection/Repairs I. Where a leakage of fluorinated greenhouse gases is detected, the operators shall ensure that the equipment is repaired without undue delay. II. Where the equipment is subject to leak checks under Article 4(1), and a leak in the equipment has been repaired, the operators shall ensure that the equipment is checked by a certified technician within one month after the repair to verify that the repair has been effective. This recheck can take place on the same day that the leak is fixed once the system has been repaired and the system has returned to balanced, normal operation. III. Where the cause of the leakage has been identified, it shall be indicated in the equipment records.
Certification Requirements I. Personnel and companies who, for a third party, install, service, maintain, repair, decommission or leak check stationary refrigeration, air conditioning, heat pump of fire protection equipment containing or relying on F-Gases must be certified under the F-Gas Regulations. II. Personnel who install, service, maintain, repair or decommission electrical switchgear containing or relying on SF6 must be certified under the F-Gas Regulations.
Equipment and Leak Checking Records The operator of equipment containing F-gases is required to maintain specified records for each piece of equipment which is subject to mandatory leak checking. Copies of F-gas records shall be maintained for at least five years and made available for inspection by the Environmental Protection Agency upon request. A copy of the records shall also be held by the contractor who carried out the work for a period of at least five years. The records must contain certain information specified by the EU F-Gas Regulations. (a) the quantity and type of fluorinated greenhouse gases installed; (b) the quantities of fluorinated greenhouse gases added during installation, maintenance or servicing or due to leakage; (c) whether the quantities of installed fluorinated greenhouse gases have been recycled or reclaimed, including the name and address of the recycling or reclamation facility and, where applicable, the certificate number; (d) the quantity of fluorinated greenhouse gases recovered; (e) the identity of the undertaking which installed, serviced, maintained and where applicable repaired or decommissioned the equipment, including, where applicable, the number of its certificate; (f) the dates and results of mandatory leak checks carried out under Article 4(1) to (3); (g) if the equipment was decommissioned, the measures taken to recover and dispose of the fluorinated greenhouse gases. Note: It is considered best practice that records of the installation, servicing, maintenance, repairing, decommissioning and leak checking of stationary refrigeration, air conditioning, heat pumps and fire protection equipment which is not subject to statutory leak checking requirements as per Article 4(1) to (3) of the F-Gas Regulation are also maintained by the operator for at least five years. Likewise, it is considered best practice that copies of such records are maintained by the contractor undertaking any such work. As the operator of equipment containing F-Gas refrigerants, you are also required under Regulation 12(2)(b) of the European Union (Fluorinated Greenhouse Gas) Regulations 2016 to establish and maintain records of the movement of any waste refrigerant gas which arises.
IMPORTANT: This document does not purport to be and should not be considered a legal interpretation of the legislation referred to herein. Although every effort has been made to ensure the accuracy of the material contained in this document, complete accuracy cannot be guaranteed. Neither the Environmental Protection Agency nor the authors accept any responsibility whatsoever for loss or damage occasioned, or claimed to have been occasioned, in part or in full as a consequence of any person acting or refraining from acting, as a result of a matter contained in this publication.

## Calc t CO2 eq
How to calculate tonnes CO2eq: The tonnes of CO2 equivalent (T CO2 eq) of an F-gas is calculated by multiplying the mass in tonnes by the Global Warming Potential (GWP) of that gas. CO2 equivalent = mass (in tonnes) * GWP For example, the tonnes CO2 equivalent of 10 kg of HFC R-404A is calculated as follows: (0.01 T) * 3,922 GWP = 39.2 tonnes Co2 eq Annex IV of Regulation (EU) No. 517/2014 of the European Parliament and of the Council of 16 April 2014 on fluorinated greenhouse gases details the method of calculating the total GWP of a mixture. https://www.epa.ie/pubs/legislation/air/ods/Regulation%20517%20of%202014%20Fgas.pdf
The GWP of common blends, HFCs, PFCs and HCFCs is provided in the ready reckoner below. If your gas does not feature on this list, you can establish its GWP and T CO2eq using the following link: https://www.unep.org/ozonaction/resources/gwp-odp-calculator/gwp-odp-calculator or downloading the app on your phone 'GWP-ODP Calculator'.
Ready Reckoner for T CO2eq | [5 empty] | IPCC data sources for more information:
Enter kgs of gas in green cells in column A below to get the tCO2eq amount in column F |  |  |  |  | AR4 values: https://www.ipcc.ch/publications_and_data/ar4/wg1/en/ch2s2-10-2.html
if a number is not entered in column A, column F will display NA (not applicable)
kgs of gas | Common Gas blends |  | GWP AR4 | tonnes CO2eq (AR4)
| R-404A |  | 3921.6 | NA
| R-407A |  | 2107 | NA
3.2 | R-407C |  | 1773.85 | 5.6763
1.25 | R-410A |  | 2087.5 | 2.6094
| R-507 |  | 3985 | NA
| R-407D |  | 1627.25 | NA
| R-407F |  | 1824.5 | NA
| R407H |  | 1495.125 | NA
| R 401A |  | 1182.48 | NA
| R 401B |  | 1288.26 | NA
| R 402A |  | 2787.8 | NA
| R 402B |  | 2416 | NA
| R 408A |  | 3151.9 | NA
| R 413A |  | 2053.1 | NA
| R 416A |  | 1084.255 | NA
| R-417A |  | 2346 | NA
| R-422A |  | 3142.95 | NA
| R 422D |  | 2728.95 | NA
| R 426 A |  | 1508.4 | NA
| R-437A |  | 1805.05 | NA
| R 438 A |  | 2264.435 | NA
| R442A |  | 1887.97 | NA
| R 508A |  | 13214 | NA
| RS45 (R434A ) |  | 3245.4 | NA
| R424A |  | 2439.6 | NA
| R448A |  | 1385.8 | NA
| R449A |  | 1396.288 | NA
| R 452 A |  | 2140.45 | NA
| R513A |  | 631.44 | NA
kgs of gas | HFC gases | HFC chemical formula | GWP Regulation (EU) No. 517/2014 | tonnes CO2eq
| HFC-23 | CHF3 | 14800 | NA
| HFC-32 | CH2F2 | 675 | NA
| HFC-41 | CH3F2 | 92 | NA
| HFC-125 | CHF2CF3 | 3500 | NA
| HFC-134 | CHF2CHF2 | 1100 | NA
| HFC-134a | CH2FCF3 | 1430 | NA
| HFC-143 | CH2FCHF2 | 353 | NA
| HFC-143a | CH3CF3 | 4470 | NA
| HFC-152 | CH2FCH2F | 53 | NA
| HFC-152a | CH3CHF2 | 124 | NA
| HFC-161 | CH3CH2F | 12 | NA
| HFC-227ea | CF3CHFCF3 | 3220 | NA
| HFC-236cb | CH2FCF2CF3 | 1340 | NA
| HFC-236ea | CHF2CHFCF3 | 1370 | NA
| HFC-236fa | CF3CH2CF3 | 9810 | NA
| HFC-245ca | CH2FCF2CHF2 | 693 | NA
| HFC-245fa | CHF2CH2CF3 | 1030 | NA
| HFC-365mfc | CH3CF2CH2CF3 | 794 | NA
| HFC-43-10mee | CF3CHFCHFCF2CF3 | 1640 | NA
kgs of gas | PFC Gases | PFC chemical formula | GWP Regulation (EU) No. 517/2014 | tonnes CO2eq (AR4)
| Sulfur hexafluoride | SF6 | 22800 | NA
| Nitrogen trifluoride | NF3 | 17200 | NA
| PFC-14 | CF4 | 7390 | NA
| PFC-116 | C2F6 | 12200 | NA
| PFC-218 | C3F8 | 8830 | NA
| PFC-c-318 | c-C4F8 | 10300 | NA
| PFC-3-1-10 | C4F10 | 8860 | NA
| PFC-4-1-12 | C5F12 | 9160 | NA
| PFC-5-1-14 | C6F14 | 9300 | NA
| PFC-c-318 | c-C4F8 | 10300 | NA
| Trifluoromethyl sulfur pentafluoride | SF5CF3 | 17700 | NA
| Perfluorocyclopropane | c-C3F6 | 17340 | NA
kgs of gas | HCFC Gas | HCFC Chemical formula | GWP AR4 | tonnes CO2eq (AR4)
| HCFC-21 | CHCl2F | 148 | NA
| HCFC-22 | CHCLF2 | 1810 | NA
| HCFC-123 | CHCl2CF3 | 77 | NA
| HCFC-124 | CHClFCF3 | 609 | NA
| HCFC-141b | CH3CCl2F | 725 | NA
| HCFC-142b | CH3CClF2 | 2310 | NA
| HCFC-225ca | CHCl2CF2CF3 | 122 | NA
| HCFC-225cb | CHClFCF2CClF2 | 595 | NA
Note on E71: Maria Lenihan: There was no GWP for AR4, the GWP assigned is from AR5