## RA and RM Checklist
RISK ASSESSMENT CHECKLIST AND SUMMARY
Item | Information | Guidance on Information to be Provided
Water Supply Zone Code | Code | Per drinking water returns | Can be automated
Water Supplier | Uisce Éireann
Scheme Name | Name | Write in the water supplier's name for the scheme | Can be automated
County | Cork
Date submitted to Supervisory Authority | 2024-10-14 | Enter the date manually (day/month/year)
Person(s) responsible for RA and RM reporting | Name | Write in the name of the appropriate contact person(s).
Was the source RA prepared due to a changed condition? | No | RA and RM plans should be submitted every 6 years, at a minimum. If a changed condition with the abstraction of source waters occurs, the water supplier must judge the need for updates to the RA and RM plan. The regulator can also request updates based on audits or learning of changes. A changed condition can be an addition or removal of an abstraction point; significant changes to abstraction rates (averages, maxima) of existing abstraction points; or configuration/layout of abstraction points. Judging significant changes to abstraction rates is subjective.
Does the source RA have a DWC delineated? | No | As per sheet RA DWC Info. Should be Y in all cases. If N, then a DWC should be delineated, and may be requested by the regulator.
Was a raw/source water quality evaluation conducted? | No | As per sheet RA RM Data Summary. Should be Y in all cases. Should be based on raw water sample from the abstraction point. If EPA data are used, then the regulator may judge the appropriateness of the data used.
Is the raw/source water quality evaluation based on data from abstraction point? | Yes | As stated in sheet RA and RM Sample locations. If N, give the ID of the monitoring station that was used and/or its coordinates.
Are there data/information gaps in the raw/source water quality evaluation? | Yes | This is a judgement call, both by the water supplier and regulator. The judgement reflects the availability of data and the characterisation of the DWC, and perceived or confirmed risks.
Are there exceedances of screening thresholds? | No | Exceedances here refers to exceedances of surface water and groundwater environmental quality standards (EQS) and/or the screening thresholds presented in Annex 5. This is not exceedances of compliance values at tap.
Parameters with exceedances | Specify | List, if applicable. Else, write 'none'. | Multiple selection functionality to be made available
Are there upward trends of any parameters? | No | Trends can only be determined with a sufficiently long-term and robust datasets. If the available datasets do not allow or trend analysis, then write 'not definable'. Whether sufficient data are available for trend analysis requires technical judgement, both by the water supplier and regulator. Where EPA monitoring data are used, EPA's publicly available trend analyses can be referenced, but it has to be recognised that this is limited in scope to nutrients for WFD status assessment purposes. Use of EPA datasets must, therefore, be assessed by water suppliers in the broader context of parameters that can affect treatment and give rise to treatment issues and delivery of unsafe water.
Parameters, substances or pollutants with upward trends | Specify | List, if definable/identifiable from the available datasets. Else, write 'none' if data are available or 'not definable' if data are not available for this purpose. | Multiple selection functionality to be made available
Are there unusual numbers or concentrations of parameters in the datasets? | No | Identify here the parameters with unusual numbers that are identified from available datasets. Unusual numbers are outliers or spikes in data series, or values that are out of normal ranges. Else, write 'none'.
Parameters with unusual numbers or concentrations | Specify | List, if applicable. Else, write 'none'. | Multiple selection functionality to be made available
Do data gaps, or exceedances, trends, or unusual number in available datasets present a risk to delivery of safe water? | No | This is a judgement call, both by the water supplier and regulator. It speaks primarily to what is known about raw water quality in context of the types and levels of treatment provided. If Y, then a narrative should be provided.
Source RA outcome | High | This is determined by the highest risk score for any identified hazard.
Identified hazards | [Specify] | List the hazards that drive the RA outcome (highest risk scores). If none, write 'none', in which case the RA outcome would be Low. | Multiple selection functionality to be made available
Hazardous events that drive the RA | C004 | Code derived from or based on Advice Note No. 8. Any hazardous events linked to hazards presenting High and Very High risk must be identified. This is informed by the DWC characterisation and firsthand knowledge of the DWC. Any identified data/knowledge gaps may trigger needs for Further Characterisation. | Multiple selection functionality to be made available
Is further characterisation recommended? | No | This is a judgement call, both by the water supplier and regulator. FC is relevant when or where data or knowledge gaps emerge. If Y, then the recommended FC should be identifiable in the RM plan.
Determination of Source RM Objective | Improve | This is a judgement call by both the water supplier and regulator. The determination is informed by the RA, especially the review of exceedances, trends and unusual numbers in the raw water quality data but also knowledge of events or circumstances that may not (yet) be supported by the available data (e.g. visible discolouration of raw water, algal blooms).
RISK MANAGEMENT CHECKLIST
Item | Information | Comment /Action
Is the source RM plan complete? | No | If N, describe missing items and proposed corrective actions.
Are suitable implementing bodies named for all recommended measures? | Yes | If N or partial, address or explain circumstances.
Are agreements in place for implementation of all recommended measures? | Yes | If N or partial, address or explain circumstances.
Are schedules of proposed or confirmed actions defined? | Yes | If N or partial, address or explain circumstances.
Are Safeguard Zones proposed? | Yes | If Y, summarise the recommended action(s). Justify.
Are there gaps in the source RM Plan? | Yes | If Y, summarise what they are and potential consequences. This is a judgement call by the RA assessor and regulator.
Do the gaps present a risk to delivery of safe water? | Yes | This is a judgment call, both by the water supplier and regulator. If Y, propose a course of action. This can be anything deemed relevant – e.g. lack of water quality data, absence of information necessary to judge risk, missing information related to RM actions, lack of documentation of treatment provided or adequacy of treatment provided.

## Scheme Info
Water Supply (Zone) Code | Water Supply Name | Treatment Plant Code | Treatment Plant Name | Max. No. Person Served | Water Supplier Contact
Code | Name | Code | Name | x | Name/phone
Comment/Action
Insert water supply scheme code. E.g. per drinking water returns | Insert water supplier's name for the scheme | Insert treatment plant code, if available/applicable | Insert water supplier's name for the treatment plant | Estimated | At discretion of water supplier (for GWS, e.g., caretaker or committee chair, and for UÉ, e.g., operations manager)
Can be automated | Can be automated | Can be automated | Can be automated

## Abstraction Info
Abstraction Point Code | Abstraction Point Name | Source Water Type | Abstraction Type | Median or Mean Daily Abstraction (m3/d) | Maximum Daily Abstraction (m3/d) | WFD WB Code SW | WFD WB Name SW | WFD Subcatchment | WFD WB Code GW | WFD WB Name GW
Code 1 | Name 1 | Surface Water | River | X | X | Code 1 | Name 1 | Code 1 | Code 1 | Name 1
Code 2 (if applicable) | Name 2 | Surface Water | Infiltration Gallery | X | X | Code 2 | Name 2 | Code 2 | Code 2 | Name 2
Code n (if applicable) | Name n | Groundwater | Well/Borehole | X | X | Code n | Name n | Code n | Code n | Name n
Comment/Action
List codes for individual abstraction points in scheme. A unique code is to be included for each abstraction point. Provided by water supplier. Can for example be based on the EPA abstraction register (recognising that this only contains abstractions >25 m3/d). | List water supplier's names for individual abstraction points | The intent here is to define the primary source of water for an abstraction point. Infiltration galleries are a special case as they can and often do capture both surface water and groundwater, but this is case-specific. Wells/boreholes can also induce flow from streams, indirectly, even if they are, primarily, sourcing groundwater. | Select abstraction point types in a given scheme | Optional. Estimated, and is relevant information for the delineation of DWC (see tab 'DWC Info') | Ideally based on records; else, estimated. Features in EPA register of abstractions. | Can be automated based on abstraction point grid coordinates; Information derived from EPA Water Maps GIS coverage. Note – lakes <50 hectares are not assigned WFD water body codes. In such instances, the information is left as n/a. | Can be automated based on abstraction point grid coordinates; Information derived from EPA Water Maps GIS coverage. | Can be automated based on abstraction point grid coordinates; Information derived from EPA Water Maps GIS coverage. | Can be automated based on abstraction point grid coordinates; Information derived from EPA Water Maps GIS coverage. Applies to groundwater-sourced abstractions. | Can be automated based on abstraction point grid coordinates; Information derived from EPA Water Maps GIS coverage. Applies to groundwater-sourced abstractions.
Can be automated | Can be automated
[6 empty] | Can be automated | Can be automated | Can be automated | Can be automated | Can be automated
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: If available

## DWC Info
Item | Drinking Water Catchment ID | DWC Area | Drawn/prepared by | Date | Filenamea,b | Land Use Description | Notes
(km2)
Abstraction Point Code 1 | Unique ID 1 | Area 1 | Person responsible/Organisation | Date 1 | Filename 1 | Dominant land uses and percentages based on GIS intersects | Unique DWC IDs for GWS can be assigned by GSI in their intended role. If DWCs for some or all abstraction points in a scheme overlap, then combined or a single DWC may be prepared, in which case combined or a single filename suffices, respectively. Such overlapping/combined DWCs must be highlighted in the RA reporting.
Abstraction Point Code 2 (if applicable) | Unique ID 2 | Area 2 | Person responsible/Organisation | Date 2 | Filename 2 | Dominant land uses and percentages based on GIS intersects
Abstraction Point Code n (if applicable) | Unique ID n | Area n | Person responsible/Organisation | Date n | Filename n | Dominant land uses and percentages based on GIS intersects
Safeguard zone 1 (if applicable) | Unique ID n | Area n | Person responsible/Organisation | Date n | Filename n | Dominant land uses and percentages based on GIS intersects | Contaminant-specific safeguard zones are prepared by EPA, based on the RA and RM process. The needs for safeguard zones are flagged by the water supplier. See implementation guidance and DHLGH (2024) for details.
Safeguard zone n (if applicable) | Unique ID n | Area n | Person responsible/Organisation | Date n | Filename n | Dominant land uses and percentages based on GIS intersects
Other Relevant Schemes Within DWC of the Scheme Being Risk Assessed, if Applicablec | Drinking Water Catchment ID | DWC Area | Contact
(km2)
Scheme 1 (name) | Unique ID n | Area n | Uisce Éireann |  |  | Example, give name
Scheme 2 (name) | Unique ID n | Area n | Group Water Scheme |  |  | Example, give name
Scheme n (name) | Unique ID n | Area n | SPS |  |  | Example, give name
Notes:
a The delineated DWCs for a scheme being assessed will be submitted electronically with a RA by the water supplier, as SHP file(s). The water suppliers will determine DWC IDs and filenames for those DWCs they produce. These will be incorporated into the register or repository of DWCs maintained by GSI. GSI will designate IDs and filenames for DWCs that they produce (e.g. on behalf of a GWS).
b The DWC shapefile file for groundwater-sourced abstraction points should be attributed with the daily mean abstraction rate as this information is used by GSI for delineation purposes.
c The DWC for an abstraction point or combined DWC for multiple abstraction points in the scheme being assessed may overlap or encompass the DWCs of other/external schemes. This is referred to as nested catchments. In such cases, the nested catchments should be identified in the RA reporting by listing the other relevant schemes. The potential presence of other relevant DWCs can be checked and obtained through the register of DWCs to be maintained by GSI.

## RA Scores
Abstraction Point | DWC ID | Hazardous Event Code | Hazardous Event Description | Likelihood | Severity | Total RA Score | Risk Assessment Matrix |  |  | Severity/Impact of Consequences
Code n | ID n | Code n | Matching description n | x | y | z |  |  |  | Insignificant | Minor | Moderate | Major | Catastrophic
Code n | ID n | Code n | Matching description n | x | y | z |  |  |  | 1 | 2 | 3 | 4 | 5
Code n | ID n | Code n | Matching description n | x | y | z | Likelihood | Almost Certain | 5
Code n | ID n | Code n | Matching description n | x | y | z |  | Likely | 4 | Sum each RA from Column G
Code n | ID n | Code n | Matching description n | x | y | z |  | Foreseeable | 3
Code n | ID n | Code n | Matching description n | x | y | z |  | Unlikely | 2
Code n | ID n | Code n | Matching description n | x | y | z |  | Most Unlikely | 1
Code n | ID n | Code n | Matching description n | x | y | z
Code n | ID n | Code n | Matching description n | x | y | z
Notes:
For GWS, this information relates to the existing RA process led by NFGWS. Specifically, the information derives from the assessment of Critical Control Point 1 (CCP 1) and the information can be extracted directly from existing CCP 1 tabulations.
UÉ's RA process is generally consistent with Advice Note No. 8, with ongoing work on hazardous event descriptions which have been amended/updated, and new ones introduced. UÉ's ranges of risk scores for different risk categories are also slightly amended, which only affects the lower risk categories, not the higher risk categories. Both UÉ and NFGWS use the same risk score range for high risk scenarios .

## WQ Sample Locations
Raw Water Sample Location | Sample Station ID | Easting | Northing | Coordinate System Given | EPA Station? | Water Supplier Station? | Other Station? | Data Type | Data Source | Other Data Source Specification
Name 1 | Station ID 1 | xxxxxxx.xx | yyyyyyy,yy | ITM | No | Yes | No | At Abstraction Point | UÉ Raw Water | Specify
Name n | Station ID 2 | xxxxxxx.xx | yyyyyyy,yy | ING | Yes | No | No | In Catchment | EPA Data | Specify
Comment/Action
Given by water supplier. If an existing EPA monitoring network station is used, then the EPA monitoring station name should be used. | Given by water supplier. If an ID is not available, then the field can be left blank. If an existing EPA monitoring network station is used, then the EPA monitoring station ID should always be used. | Only required if raw water sample is not taken from the abstraction point inlet or an EPA monitoring station. | Only required if raw water sample is not taken from the abstraction point inlet or an EPA monitoring station. | Indicate which coordinate system the coordinates are given in. | Verify if the sample station used for the water quality assessment is an EPA monitoring station. | Verify if the sample station used for the water quality assessment is an water supplier monitoring station. | Verify if the sample station used for the water quality assessment is the monitoring station of a third party. | Indicate the nature of the data used – raw water at abstraction point or in the DWC, or a treated water sample. | Indicate the source of the data used. | If the data were not sourced from the water supplier or EPA, then specify.

## WQ Data Screening Values
Parameter | Screening Value Used by NFGWS | Annual Mean Value (AMV) or Max Value | Screening Value Used by UÉ | Annual Mean Value (AMV) or Max Value | Unit | Comment
Surface Water
E.Coli | 1000 | Max | 1000 | Max | counts/100 mL | Alternatively, what is deemed appropriate for the site-specific circumstances of the source water. Note, the source of all NFGWS screening values in this tab is Appendix 1 of https://nfgws.ie/wp-content/uploads/2019/06/NFGWS-A-Framework-for-Drinking-Water-Source-Protection.pdf
Nitrate as NO3 | 28 | AMV | 30 | Max | mg/L | For NFGWS, the 28 mg/l value is 75% of the Groundwater Threshold Value (TV) on the Groundwater Regulations intended to prevent exceedances of the Maximum Allowable Concentration of 50 mg/L. It is also used by the EPA as a target to reduce the likelihood of exceeding the TV. For UÉ, the 30 mg/L max value is in line with their Treatment Barrier Risk score 3 and above.
Ammonium as N | 0.175 | AMV | 0.14 | Max | mg/L | The parametric value in the Regulations is quoted as NH4 whereas in both the Groundwater and Surface Water Regulations values are given as N. The conversion factor from NH4 to N is 0.778. The WFD Good status boundary of 0.14 mg/L is used by UÉ, and is the 95%ile EQS for total ammonia as N. UÉ reports data as NH4. Note, the WHO estimates that water containing more than 0.2 mg/L of ammonia at the point of disinfection may react with and disable 68% of chlorine added for disinfection.
Phosphate as P | 0.035 | AMV | 0.035 | AMV | mg/L | Used for rivers; annual mean value = WFD Good status boundary. Molybdate Reactive Phosphorus or Orthophosphate
Total Phosphorus as P | 0.02 | AMV | 0.025 | AMV | mg/L | Used for lakes; annual mean value = WFD Good status boundary
Colour | 100 | Max | 100 | Max | mg/L Pt/Co (mg/L Hazen) | Max. value. Alternatively, UÉ considers what is deemed appropriate for the site-specific circumstances of the source water
MCPA (specific) | 0.075 | AMV | -- | -- | µg/L | For NFGWS, the 0.075 µg/l value represents 75% of the DWS and has been adopted as a target to reduce the likelihood of exceeding 0.1 µg/l.
Individual Pesticide (includes MCPA) | -- | -- | 0.05 | Max | µg/L | UÉ uses half the DWS in line with its current approach for highlighting a risk.
Total Pesticides | 0.375 | AMV | 0.25 | Max | µg/L | For NFGWS, the 0.375 µg/l value represents 75% of the DWS and has been adopted as a target to reduce the likelihood of exceeding 0.5 µg/L. UÉ uses half the DWS in line with its current approach for highlighting a risk.
Polycyclic Aromatic Hydrocarbons | 0.075 | AMV | 0.075 | Max | µg/L
Benzo(a)pyrene | 0.0075 | AMV | -- | -- | µg/L
Manganese | -- | -- | 30 | Max | µg/l | Alternatively, UÉ considers what is deemed appropriate for the site-specific circumstances of the source water. Values above 30 µg/L can cause issues in the network and discoloration.
Turbidity | -- | -- | 10 | Max | NTU | Alternatively, UÉ considers what is deemed appropriate for the site-specific circumstances of the source water. Values above 10 NTU can cause treatment issues.
Groundwater
E.Coli | 100 (boreholes) or 1000 (springs) | Max | 100 (boreholes) or 1000 (springs) | Max | counts/100 mL | See comment above for surface water.
Nitrate as NO3 | 28 | AMV | 30 | Max | mg/L | See comment above for surface water.
Ammonium as N | 0.175 | AMV | 0.14 | Max | mg/L | See comment above for surface water.
Phosphate as P | 0.035 | AMV | 0.035 | AMV | mg/L | Alternatively, UÉ considers what is deemed appropriate for the site-specific circumstances of the source water.
Colour | 20 | Max | 20 | Max | mg/L Pt/Co (mg/L Hazen)
MCPA (specific) | 0.075 | AMV | -- | -- | µg/L | For NFGWS, the 0.075 µg/l value represents 75% of the DWS and has been adopted as a target to reduce the likelihood of exceeding 0.1 µg/l.
Individual Pesticide (includes MCPA) | -- | -- | 0.05 | Max | µg/L | UÉ uses half the DWS in line with its current approach for highlighting a risk.
Total Pesticides | 0.375 | AMV | 0.25 | Max | µg/L | For NFGWS, the 0.375 µg/l value represents 75% of the DWS and has been adopted as a target to reduce the likelihood of exceeding 0.5 µg/L. UÉ uses half the DWS in line with its current approach for highlighting a risk.
Manganese | -- | -- | 30 | -- | µg/l | Alternatively, what is deemed appropriate for the site-specific circumstances of the source water. UÉ notes that values above 30 µ/L can cause issues in the network and discoloration.
Iron | -- | -- | 150 | -- | µg/l | Alternatively, what is deemed appropriate for the site-specific circumstances of the source water.
Benzo(a)pyrene | 0.0075 | -- | -- | -- | µg/L | Annual mean value
Aldrin | 0.0225 | AMV | -- | -- | µg/L | Not listed in NFGWS (2019), but is being considered by NFGWS. UÉ considers individual pesticides in raw water on a risk basis.
Dieldrin | 0.0225 | AMV | -- | -- | µg/L
Heptachlor | 0.0225 | AMV | -- | -- | µg/L
Heptachlor epoxide | 0.0225 | AMV | -- | -- | µg/L
Bentazone | 0.075 | AMV | -- | -- | µg/L

## WQ Data Summary
Sample Station ID | DWC Code | Data Type | Data Source | Parameter | Parameter Unit | Reporting Period (Years) | No. Samples in Reporting Period | No. Values > LOQ | Average | Maximum | No. of Samples >Screening Value | Percent Samples >Screening Value | Trend Comments | Unusual Numbers (Suspected Outliers) Comments | Other Comments
Station ID 1 | Code 1 | In Catchment | EPA Data | Colour | mg/L pt/Co | 2015-2011 | n | n | n | n | n | n | None | Spikes every winter | Peaty catchment
Station ID 1 | Code 1 | In Catchment | EPA Data | Total Ammonia as N | µg/L | 2007-2023 | n | n | n | n | n | n | Upward 2011-2019, exceeding the surface water EQS in 2018, then downward thereafter | -- | Peat extensively drained
Station ID 1 | Code 1 | In Catchment | EPA Data | Bentazone | µg/L | 2016-2024 | n | n | n | n | n | n | None | -- | Detections in spring samples
Station ID 2 | Code 2 | In Catchment | EPA Data | Phosphate as P | µg/L | 2022-2024 | n | n | n | n | n | n | None | -- | Above screening value but below DWS
Station ID n | Code n | Treated Water | UÉ Data | Bentazone | µg/L | 2007-2023 | n | n | n | n | n | n | None | One outlier (September 2020) | Generally below screening values
Comment/Action
Given by water supplier. If an ID is not available, then a station name or location descriptor should be provided. If an existing EPA monitoring network station is used, then the EPA monitoring station ID should always be used. | -- | -- | -- | Information taken from a water quality database which is to be shareable with EPA | -- | -- | These fields are populated by the water supplier based on the water supplier's queries of data. Exceedances of screening values are used to identify hazards. Average concentrations can only be calculated with a reasonably large population of data, and values below detection limits will be considered as values which are equal to half the detection limit. Averages cannot be calculated if all data are below the detection limit. It is recognised that detection limits can vary in the available datasets. Reporting in exceedances, trends and unusual numbers requires technical judgement. | [5 empty] | Judgement call, based on data analysis. Should be brief but sufficiently detailed for regulatory verification. | Judgement call, based on review of data. Should be brief but sufficiently detailed for regulatory verification. | Any helpful information that is relevant to the
This table serves to summarise the potential hazards which will assist EPA's reporting requirements in context of Regulation 16
This table has been filled in with fictional information, for illustration purposes.

## RM Plan
Measure No. | Abstraction Point Code | DWC ID | Identified Hazard | Hazardous Event Code | Planned Action | Action Type | Action Title | Planned Schedule | Target Completion Date | Implementing Body | Agreements in Place | Action Status | Are Necessary Resources Secured | Funding Stream | Implementation Constraints | Additional Comment
1 | AP Code 1 | DWC Code 1 | MCPA | C040 | Identify users and reduce MCPA usage in the DWC | Preventive | Implementation of the GAP Regulations and the Sustainable Use of Pesticides Regulations | Long-term | End 2033 | Local Authority | Partially | In Progress | N/A | N/A | -- | Water supplier and LA coordinating with DAFM-PRCD to establish and enforce pesticide safeguard zones under the Sustainable Use of Pesticides Regulations. Outreach activity is led by the LA.
2 | AP Code 1 | DWC Code 1 | MCPA | C040 | Routine raw water monitoring at the abstraction point | Monitoring | Raw water monitoring at abstraction point | Long-term | Ongoing | Group Water Scheme | Yes | In Progress | Yes | Governmental | -- | Raw water monitoring at the abstraction point to date is insufficient. MCPA is detected in the DWC based on review of EPA data. The recommended monitoring will be focused on a pesticide suite, but also an expanded suite of parameters to include nutrients. Quarterly.
3 | AP Code 2 | DWC Code 2 | Phosphate | C040 | Targeted monitoring downstream of High PIP-P areas | Monitoring | Targeted catchment monitoring | Short-term | End 2028 | Group Water Scheme | Yes | In Preparation | Yes | Governmental | -- | Elevated orthophosphate is detected in EPA data. Source area is unknown. 'Targeted monitoring, bi-weekly, at seven selected locations, over one year.
4 | AP Code 2 | DWC Code 2 | Phosphate | C040 | Reduce episodic nutrient loads to river, especially phosphates | Mitigation | Establish buffer zones in confirmed High PIP-P areas | Long-term | End 2030 | ASSAP | No | Unclear, TBD | No | Governmental | Potentially, funding and commitments | No immediate plans for action. ASSAP has been approached for possible assistance. Action to be further defined following outcome of Measure No. 3. TBD in near-term.
Comment/Action
Sequential, defined by water supplier | Identifies the relevant abstraction which may be at risk | Identifies the DWC the action is linked with | The hazard | The hazardous event the risk is linked with | The text is defined by the water supplier to indicate the nature of the relevant action that is planned. | This defines the type of measure that is planned, which falls into three categories: preventive (statutory); mitigation (voluntary); and monitoring (necessary to learn, track and judge) | The text is defined by the water supplier to name the action that is planned |  |  | For any given action, multiple implementing bodies may be apply |  |  |  |  | Brief narrative | Relevant commentary on measure. Regulator may ask for details/specifics in a review of audit situation.
Multiple selection functionality to be made available
Note:
The level of details to be provided on measures is subjective. It will be initiated by the water suppliers and will be case-specific, but should be sufficient to communicate the 'why', 'how' and 'when for each hazard and risk. The Table 1 of Integrated Source Protection Plans produced by the NFGWS can serve to steer the level of reporting. ISPPs can be sourced from the NFGWS upon request.
The template above will be updated in 6-year cycles, or as changed conditions occur. It will be informed by lessons learnt and recommendations from the RM tracking in the previous reporting cycle. Existing measures may be amended/updated and new measures added. It is informed by risks and learning.
THE TABLE ABOVE IS ILLUSTRATIVE, NOT BASED ON A REAL EXAMPLE. IT HAS BEEN FILLED IN TO INDICATE THE KIND OF INFORMATION THAT IS RELEVANT, AND A SUGGESTED LEVEL OF DETAIL.

## RM Plan Tracking
Measure No. | Action Title | Did the Measure Prove Effective? | Lesson Learned | Constraints | Recommended Further Action
1 | Implementation of the GAP Regulations and the Sustainable Use of Pesticides Regulations | Yes, fewer MCPA detections overall are being recorded, although elevated MCPA detections above the screening threshold still occur, mainly in spring and summer samples. | Community outreach on pesticide usage is necessary every year, prior to the main pesticide application period. | Staff turnover and maintaining momentum with the measure. Record-keeping of pesticides applied remains poor. | Continuation of measure. Improvements are still possible.
2 | Raw water monitoring at abstraction point | Yes, monitoring was conducted as planned and the data produced are informative. Elevated turbidity concentrations were noted periodically. Ammonia detections above its threshold also occurs sporadically. | -- | Expense of monitoring. It is uncertain how long the monitoring can be maintained at the level planned. Additional sourcing of funds will be necessary. | Continuation of measure. Adapted (reduced) sampling for MCPA, still monthly but limited to the period April–September. Quarterly monitoring to continue for all other parameters. Turbidity and ammonia to receive greater attention overall.
3 | Targeted catchment monitoring | Yes, the monitoring provided illustrative results. Source areas of phosphate were identified. Two new potential hazards were also identified – specifically, turbidity and ammonia in a stream near a cluster of houses. | The investigative monitoring was conducted around major rainfall events, thus catching P-loading events. The related catchment walks identified areas of significant soil erosion at multiple livestock access points, both to streams and in field drains. | -- | Proceed with Measure 4 to reduce P-loading. Conduct inspections of septic tanks and/or percolation systems in cluster of houses identified as a potential sources of ammonium (a new Measure 5). Address livestock access to streams and field drains (a new Measure 6).
4 | Establish buffer zones in confirmed High PIP-P areas | N/A. This was identified as a potential future measure. Its scope is now informed by Measure No. 3. The scope will be defined in the updated RM Plan. | Measures Nos 1 and 3 helped to identify key (influential) stakeholders in the community. | -- | Establish vegetated buffer zones along Stream X. Expand vegetated buffer zones along field drains previously not identified. Restrict livestock access to Stream X and field drains. Convincing farmers will be necessary.
Note:
The updating of RA and RM plans is a continuous process, in 6-year cycles or as changed conditions occur. RM Plan tracking is iterative. The updated RA for the subsequent reporting cycle will incorporate the new data and information from RM activity, as well as the learning during the current reporting cycle. RM plans will be updated to include the recommendations in Column E.
THE TABLE ABOVE IS ILLUSTRATIVE, NOT BASED ON A REAL EXAMPLE. IT HAS BEEN FILLED IN TO INDICATE THE KIND OF INFORMATION THAT IS RELEVANT. IT ACCOMPANIES THE PREVIOUS TAB 'RM PLAN' AND CAN ONLY BE COMPLETED AFTER THE FIRST CYCLE OF RM IMPLEMENTATION'

## Lists for Dropdowns
Counties | Yes | Yes | Improve | Uisce Éireann | Low | Hazardous Description Code | Yes | Surface Water | River | At Abstraction Point | UÉ Data | ITM | mg/L | Immediate | Preventive | Yes | Inactive | Water Supplier
Carlow | No | No | Protect | Group Water Scheme | Medium | C001 | No | Groundwater | Lake | In Catchment | GWS Data | ING | µg/L | Short-term | Mitigation | No | In Progress | Governmental
Cavan | Partial | Uncertain |  | SPS | High | C002 | Insufficient data | SW and GW | Impounded Reservoir | Treated Water | EPA Data |  | NTU | Medium-term | Monitoring | N/A | In Preparation | Grant
Clare |  |  |  |  | Very High | C003 |  |  | Well/Borehole |  | Local Authority Data |  | Counts per 100 mL | Long-term |  |  | Unclear, TBD | Other
Cork | [5 empty] | C004 |  |  | Spring |  | Other |  | mg/L Pt/Co (mg/L Hazen) |  |  |  | Potential future | N/A
Donegal | [5 empty] | C005 |  |  | Infiltration Gallery | [7 empty] | Completed
Dublin |  | Yes |  |  |  | C006
Galway |  | No |  |  |  | C007
Kerry |  | Partially |  |  |  | C008
Kildare | [5 empty] | C009
Kilkenny | [5 empty] | C010
Laois | [5 empty] | C011 |  |  |  | Uisce Éireann
Leitrim | [5 empty] | C012 |  |  |  | Group Water Scheme
Limerick | [5 empty] | C013 |  |  |  | EPA
Longford | [5 empty] | C014 |  |  |  | Local Authority
Louth | [5 empty] | C015 |  |  |  | LAWPRO
Mayo | [5 empty] | C016 |  |  |  | ASSAP
Meath | [5 empty] | C017 |  |  |  | DAFM-PRCD
Monaghan | [5 empty] | C018 |  |  |  | Community
Offaly | [5 empty] | C019 |  |  |  | Other Public Body
Roscommon | [5 empty] | C020 |  |  |  | Third Party
Sligo | [5 empty] | C021
Tipperary | [5 empty] | C022
Waterford | [5 empty] | C023
Westmeath | [5 empty] | C024
Wexford | [5 empty] | C025
Wicklow | [5 empty] | C026
C027
C028
C029
C030
C031
C032
C033
C034
C035
C036
C037
C038
C039
C040
C041
C042
C043
C044
C045
C046
C047
C048
C049
C050
C051