## Introduction
Organisation Name
Licence Number
Completed By | Name
Position
Email
Direct Tel.
Date:
This Fire Water Retention Risk Assessment Spreadsheet is to be used in conjunction with the EPA Guidance on Retention Requirements for Firewater Run-off. The purpose of this workbook is to determine, at a conservative level, whether firewater retention is required for the facility, and if so the required retention capacity.
SHEET DESCRIPTION |  | INSTRUCTIONS | COMMENT
Significance of Fire Event |  | Please enter the fire protection measures that are available in each area of the site and the quantity of flammable and combustible material storage within these areas. | Input Required
Hazard Potential |  | Please enter the quantities of hazardous substances stored within each "assessment area" of the site. If the site is a licensed waste disposal facility please select "Hazardous" or "Non-Hazardous", or "N/A" if this does not apply. | Input Required
Fire Water Run-Off Risk |  | This tab will outline the Overall Fire Water Run-Off Risk of each area based on the Significance of a Fire event and the Hazard Potential in each "assessment area". The conclusion as to whether or not the site requires fire water retention is stated here. | Risk Assessment Result
Information |  |  | Further Information
Method 1: Warehouse Retention Calculation |  | A calculation of the fire water retention required for a warehouse area storage is outlined here. The method is based on the Swiss Federation Firewater Retention Practical Guide. | Input Required
Method 2: Tank Farm / Process Plant Retention Calculation |  | For other areas, e.g. tank farm, process room, etc. a detailed assessment should be carried out to determine firewater retention volume required. This involves acquiring information on expected fire duration, sprinkler flow rates, etc. See Section 4.3 of the Guidance Report. | Input of Calculation and Support Data
Method 3: General Retention Calculation |  | A generic calculation can also be used based on first principles of fire water retention. This is a conservative approach to retention volume calculation. | Input Required
FIRE WATER RETENTION RISK ASSESSMENT

## Significance of Fire Event
Sample Assessment Area
Number | Fire Protection Measures in this Area | Response
1. Fire Prevention Measures
1.1 | Fire Detection and Alarm Systems (FDAS). IS 3218:2013 | Yes | 0
1.2 | Automatic Fire Protection | No | 1
2. Materials Stored |  | Tonnes |  | Substance Name(s)
| H224 (extremely flammable) | 0 |  |  | Tonnes
| H225 (highly flammable) | 0 |  |  | Tonnes
| H226 (flammable)1 | 0 |  |  | Tonnes
2.1 | Flammable Liquids Storage | 0 | 0 |  | Tonnes
| H220 (extremely flammable) | 0 |  |  | Tonnes
| H221 (flammable) | 0 |  |  | Tonnes
2.2 | Flammable Gas Storage | 0 | 0 |  | Tonnes
| H228 (flammable) | 0 |  |  | Tonnes
2.3 | Flammable Solids Storage | 0 | 0 |  | Tonnes
| H227 Combustible Liquids | 0 |  |  | Tonnes
| Waste | 0 |  |  | Tonnes
| Packaging (including pallets) | 0 |  |  | Tonnes
| Plastic (if not in packaging above) | 0 |  |  | Tonnes
| Oils/fuels (not classified as flammable) | 0 |  |  | Tonnes
| Process materials (not classified as flammable) | 0 |  |  | Tonnes
| Any other combustible material | 0 |  |  | Tonnes
2.4 | Combustible Materials Storage | 0 | 0 |  | Tonnes
| Percent of S1 Storage | 0% | N/A
| Percent of S2 Storage | 0% | N/A
| Percent of S3 Storage | 0% | N/A
0
|  |  | 2. Max |  | 0
|  | Fire Significance |  |  | S1 - Low Significance
| Likelihood | Description
| S 1 | Low Significance
| S 2 | Medium Significance
| S 3 | High Significance
Scoring Details
| Flammable Material Threshold (see Information Tab for Threshold details) | Fire Protection |  | Significance
| None | N/A |  | S 1
| Lower | FDAS |  | S 1
| Lower | None |  | S 2
| Middle | FDAS Sprinklers |  | S 1
| Middle | FDAS |  | S 2
| Middle | None |  | S 3
| Upper | Any |  | S 3
Note 1 | H226 Flammable Liquids have a large flash point range. Higher flash point flammables (e.g. Diesel - Flash Point 55-56°C) can be considered as combustible for the purpose of this exercise if the material under normal environmental or workplace operational conditions will always be handled at temperatures at least 15ºC below their flashpoint and in consequence will not produce a flammable atmosphere. See HSG140 - Safe Use and Handling of Flammable Liquids, UK HSE 2015, for more information. Ambient external temperature in Ireland does not generally exceed 30ºC. See Appendix A of Guidance Report for more information.
Flammable Substance Thresholds (Tonnes)
| Threshold | Flammable Liquid |  | Flammable Solids | Flammable Gas | Combustibles
| Upper | ≥50 |  | ≥10 | ≥5 | ≥200
| Middle | ≥5 - <50 |  | ≥0.5 - <10 | ≥0.1 - <5 | ≥30 - <200
| Lower | ≥0.1 - <5 |  | ≥0.05 - <0.5 | ≥0.01 - <0.1 | ≥2 - <30
| None/ Negligible | <0.1 |  | <0.05 | <0.01 | <2
FURTHER INFORMATION
Significance of Fire Event

## Pathways (hidden)
Warehouse Area |  |  |  |  | Process Area |  |  |  |  | Area C
Number | Destination of Run-off from this Area | Response |  | Pathway Consequence | Number | Destination of Run-off from this Area | Response |  | Pathway Consequence | Number | Destination of Run-off from this Area | Response |  | Pathway Consequence
1.1 | Collection in site drainage system and stored in dedicated retention system within the operational site | Yes | 0 | P0 | 1.1 | Collection in drainage system and stored in dedicated retention system within the operational site | No | 0 | P0 | 1.1 | Collection in drainage system and stored in dedicated retention system within the operational site | No | 0 | P0
1.2 | Collection in site drainage system and sent to onsite WWTP | No | 0 | P1 | 1.2 | Collection in site drainage system and sent to the sites own WWTP (capable of handling material) | No | 0 | P1 | 1.2 | Collection in site drainage system and sent to the sites own WWTP (capable of handling material) | No | 0 | P1
1.3 | Direct run-off into local authority sewer | Yes | 2 | P2 | 1.3 | Direct run-off into local authority sewer | No | 0 | P2 | 1.3 | Direct run-off into local authority sewer | No | 0 | P2
1.4 | Direct run-off into environment | No | 0 | P3 | 1.4 | Direct run-off into environment | No | 0 | P3 | 1.4 | Direct run-off into environment | No | 0 | P3
|  | 1. Max | 2 |  |  |  | 1. Max | 0 |  |  |  | 1. Max | 0
2.1 | In the event of a fire, will the fire alarm automatically shut off valve in drainage system to prevent release ? | No | 0 | (Reduction of consequence P2 to P1) | 2.1 | In the event of a fire, will the fire alarm automatically shut off valve in drainage system to prevent release | No | 0 | (Reduction of consequence P2 to P1) | 2.1 | In the event of a fire, will the fire alarm automatically shut off valve in drainage system to prevent release | Yes | 0 | (Reduction of consequence P2 to P1)
|  |  |  | 2 |  |  |  |  | 0 |  |  |  |  | 0
| Consequence Rating | Description |  | Scoring |  | Consequence Rating | Description |  | Scoring |  | Consequence Rating | Description |  | Scoring
| P 0 | No Risk |  | 0 |  | P 0 | No Risk |  | 0 |  | P 0 | No Risk |  | 0
| P 1 | Low Risk |  | 1 |  | P 1 | Low Risk |  | 1 |  | P 1 | Low Risk |  | 1
| P 2 | Medium Risk |  | 2 |  | P 2 | Medium Risk |  | 2 |  | P 2 | Medium Risk |  | 2
| P 3 | High Risk |  | 3 |  | P 3 | High Risk |  | 3 |  | P 3 | High Risk |  | 3
|  | Containment/ Pathways |  | P2 - Medium Risk |  |  | Containment/ Pathways |  | P0 - No Risk |  |  | Containment/ Pathways |  | P0 - No Risk
Containment/ Pathways
Containment/ Pathways
Containment/ Pathways

## Environmental Consequences (hidden)
Warehouse Area |  |  |  |  | Process Area |  |  |  |  | Area C
Sheet Reference |  |  | Score | Lookup Value | Sheet Reference |  |  | Score | Lookup Value | Sheet Reference |  |  | Score | Lookup Value
Hazard Potential |  |  | H0 - No Hazard Potential | H0 | Hazard Potential |  |  | #REF! | #REF! | Hazard Potential |  |  | #REF! | #REF!
Pathways |  |  | P2 - Medium Risk | P2/P3 | Pathways |  |  | P0 - No Risk | P0/P1 | Pathways |  |  | P0 - No Risk | P0/P1
| P0/P1 | P2/P3 |  |  |  | P0/P1 | P2/P3 |  |  |  | P0/P1 | P2/P3
H0 | C0 | C1 |  |  | H0 | C0 | C1 |  |  | H0 | C0 | C1
H1 | C2 | C3 |  |  | H1 | C2 | C3 |  |  | H1 | C2 | C3
H2 | C3 | C3 |  |  | H2 | C3 | C3 |  |  | H2 | C3 | C3
H3 | C3 | C3 |  |  | H3 | C3 | C3 |  |  | H3 | C3 | C3
|  |  | Score | Lookup Value |  |  |  | Score | Lookup Value |  |  |  | Score | Lookup Value
Environmental Consequences |  |  | C1 - Limited Environmental Damage Potential | C1 | Environmental Consequences |  |  | #REF! | #REF! | Environmental Consequences |  |  | #REF! | #REF!
Environmental Consequences
Environmental Consequences
Environmental Consequences
Environmental Consequences
Environmental Consequences

## Hazard Potential
Sample Assessment Area
Number | Material Stored in this Area | Response |  | Hazard Category
1. Hazardous Material Storage on Site3
1.1 | H400/H410 Environmentally Hazardous Material (GHS Classification) (tonnes) | 0
1.2 | H401/411 Environmentally Hazardous Material (GHS Classification) (tonnes) | 0
1.3 | H402/412 Environmentally Hazardous Material (GHS Classification) (tonnes) | 0
1.4 | H413 Environmentally Hazardous Material (GHS Classification) (tonnes) | 0
| Total H400 Equivalent Material | 0 | 0 | H0
Note on WGK Classification: Use either H statement or WGK classification of a material. Start with H statement if available, if not available use WGK classification instead. DO NOT ENTER THE SAME MATERIAL UNDER BOTH CLASSIFICATIONS See Appendix A of the Guidance Document for further instruction
1.5 | WGK3 Water Hazardous Material (German Classification) (tonnes) | 0
1.6 | WGK2 Water Hazardous Material (German Classification) (tonnes) | 0
1.7 | WGK1 Water Hazardous Material (German Classification - See information tab) (tonnes) | 0
| Total WGK3 Equivalent Material | 0 | 0 | H0
1.8 | Laboratories which contain Genetically Modified Micro-Organisms (GMOs) According to Directive 2009/41/EC (Groups 3 & 4) See Appendix A of the Guidance Document for further instruction. | No | 0 | H0
1.9 | Licensed Hazardous Waste Facility | No | 0 | H0
|  |  | Max | 0
|  | Hazard Potential |  | H0 - No Hazard Potential
Hazard Potential | Description
H0 | No Hazard Potential
H1 | Hazard Potential
Scoring Details
Hazard Potential | Quantity of Material / Type of Facility
H0 | <1t WGK 3 or Equivalent1
No hazard potential | <1t Toxic (H400/H410 Harmful to Aquatic Life) or Equivalent2
H1 | >1t WGK 3 or Equivalent1
Hazard potential | <1t (H400/H410 Harmful to Aquatic Life) or Equivalent2
Laboratories Which Contain Genetically Modified Micro-Organisms (GMOs) According To Directive 2009/41/EC (Groups 3 & 4)
Licenced Waste Storage Facility
Note 1: Hazardous to the Aquatic Environment Equivalent Calculation: 100t H412/H413 = 10t H411 = 1t H400/410
Note 2: WGK Equivalent Calculation: 100t WGK1 = 10t WGK2 = 1t WGK3
Note 3: Fire-fighting foam to be used in this area should be included if relevant hazard classifications apply
Hazard Potential: The ECHA Chemical Database contains information for the safe handling of hazardous substances and other chemical substances at work. Furthermore the user is offered information on important physical and chemical properties as well as special regulations e.g. GHS classification and labelling according to CLP regulation (pictograms, H phrases, P phrases).
https://echa.europa.eu/
The GESTIS database provides WGK ratings for the majority of substances.
http://www.dguv.de/ifa/gestis/gestis-stoffdatenbank/index-2.jsp
Examples of some commonly used substance on industrial sites in large quantities;
Substance/Material | Flammable or Environmental H-Statements | Water Hazard Class
(WGK)
Acetic Acid | H226: Flammable liquid and vapour | 1
Acetone | H225: Highly flammable liquid and vapour | 1
Aqueous Ammonia | H400: Very toxic to aquatic life | 2
Chlorine | H400: Very toxic to aquatic life | 2
Chromic Acid | H410: Very toxic to aquatic life with long lasting effects | 3
Copper Sulphate | H400: Very toxic to aquatic life | 3
H410: Very toxic to aquatic life with long lasting effects
Cyclohexane | H225: Highly flammable liquid and vapour | 2
H400: Very toxic to aquatic life
H410: Very toxic to aquatic life with long lasting effects
Diesel | H226: Flammable liquid and vapour | 2
*(Diesel can be considered combustible liquid for FWRA Tool as per Appendix A, Section 1.2.3)
H411: Toxic to aquatic life with long lasting effects
Ethanol | H225: Highly flammable liquid and vapour | 1
Heptane | H225: Highly flammable liquid and vapour | 2
H400: Very toxic to aquatic life
H410: Very toxic to aquatic life with long lasting effects
Hydrochloric Acid | No environmental or flammable H-Statement assigned | 1
Isopropanol | H225: Highly flammable liquid and vapour | 1
Isobutanol | H226: Flammable liquid and vapour | 1
Methanol | H225: Highly flammable liquid and vapour | 1
Methyl tert-butyl ether (MTBE) | H225: Highly flammable liquid and vapour | 1
Phenol | H411: Toxic to aquatic life with long lasting effects | 2
Sodium Nitrite | H400: Very toxic to aquatic life | 2
Tetrahydrofuran | H225: Highly flammable liquid and vapour | 1
Toluene | H225: Highly flammable liquid and vapour | 2
Trichloroacetic Acid | H400: Very toxic to aquatic life | 2
H410: Very toxic to aquatic life with long lasting effects
Trichloroethylene | H412: Harmful to aquatic life with long lasting effects. | 3
2,2,4-Trimethylpentane | H225: Highly flammable liquid and vapour | 2
H400: Very toxic to aquatic life
H410: Very toxic to aquatic life with long lasting effects
Zinc Chloride | H400: Very toxic to aquatic life | 3
H410: Very toxic to aquatic life with long lasting effects
Hazard Potential

## Firewater Run-Off Risk
Sample Assessment Area
Sheet Reference |  |  | Score | Lookup Value
Signficance of Fire Event |  |  | S1 - Low Significance | S1
Hazard Potential |  |  | H0 - No Hazard Potential | H0
| H0 | H1
S1 | R0 | R1
S2 | R0 | R1
S3 | R1 | R1
|  |  | Score | Lookup Value
Fire Water Run-Off Risk |  |  | R0 - No Risk | R0
Risk |  | Minimum Firewater Retention Measures Required
R0 No Risk |  | No dedicated firewater retention required.
R1 Limited Risk |  | The fire-water run-off must be retained within the operational site. Operational or emergency response teams must by means of emergency response procedures establish temporary retention facilities by the use of mobile systems (e.g. sand bags, movable barriers etc.)
R1 Risk of Environmental Contamination |  | Firewater run-off must be retained within the operational site. The retention can be provided by means of the site's drainage system and other suitable infrastructure which is not exclusively foreseen for firewater retention (e.g. storm water ponds / tanks in waste water treatment plants). All elements of the site infrastructure to be used for firewater retention (including shutoff valves) must be regularly inspected to ensure functionality and impermeability. The retention facility must remain impermeable for the duration of the incident up to the removal of the firewater run-off The documented available retention capacity in the existing site infrastructure must be monitored and maintained. Automatic shut-off valves must be maintained and tested. Diversion of firewater to retention facilities must be automatic on activation of the site fire alarm. Onsite bunds cannot be used to provide firewater retention unless the content of a bund is directly involved in the fire event.
Conclusion
Fire Water Retention Required on Site? |  |  | No
Overall Fire Water Run-Off Risk

## Data (hidden)
Fire Likelihood |  |  |  |  | Hazard Potential |  |  | Warehouse Fire Water Retention Caluclation
Listed Activities | Score (Fire Likelihood) | 1. Fire Prevention Measures |  |  | Listed Activities | Score |  | Types of Storage | Factor
Minerals and Other Materials | 4 | FDAS | Yes | 0 | Yes | 1 |  | Non-racked Storage | 1
Metals | 4 |  | No | 1 | No | 0 |  | Rack: Height <6m | 2
Mineral Fibres and Glass | 4 |  | N/A | 0 |  |  |  | Rack: Height = 6m - 12m | 3
Chemicals | 4 | [6 empty] | Rack: Height >12m | 4
Food and Drink | 4 | Sprinklers | Yes | 0
Textiles and Leather | 4 |  | No | 1 |  |  |  | Tank Farm/ Process Area Retention Calculation
Fossil Fuels | 4 |  | N/A | 0 |  |  |  | Evaporation of FW | 25%
Cement | 4 | [6 empty] | Fire Event Hours | 6 | hours
Waste (class 11.1) | 8 | FPA | Yes | 0 |  |  |  | Rain Event 1 in 20 year | 0.055 | m
Surface Coatings | 4 |  | No | 1
Other Activities (includes testing of engines, manufacture of integrated circuits and printed circuit boards, production of lime and manufacture of ceramics) | 0 |  | N/A | 0
Prevention Measure | Score Weighting
FDAS | 1 |  |  |  | GMOs | No | 0
Sprinklers | 1 |  |  |  |  | Yes | 1
FPA | 1
Total | 3
Medium Likelihood Threshold | 1
High Likelihood Threshold | 2

## Method 1 Warehouse Calculation
Warehouse Area
Number | Calculation Steps | Response |  | Comment
1.1 | Size of Storage Area (m2) | 0 | 0 | Input Required
1.2 | Flammable Material (tonnes) | 0 |  | From Significance tab
1.3 | Combustible Material (tonnes) | 0 |  | From Significance tab
1.5 | Aerosol materials, not already classified as flammable - H222, H223 (tonnes) | 0 |  | Input Required
1.6 | Oxidising Material not already classified - H270, H271 (tonnes) | 0 |  | Input Required
1.7 | Oxidising Material not already classified - H272 (tonnes) | 0 |  | Input Required
1.4 | Non Combustible Material (tonnes) (see note 1) | 0 |  | Input Required
1.8 | Total F1/F2 Materials | 0
1.9 | Total F3/F4 Materials | 0
1.1 | Total Storage in this Area (tonnes) | 0 | 0
1.11 | Fire Hazard Category | N/A | N/A
1.12 | Storage Density (kg/m2) | #DIV/0!
1.13 | Storage Density Factor | #DIV/0!
1.14 | Type of Storage | Non-racked Storage | 1 | Input Required
| Preliminary Fire Water Retention Required m3 (without storage density factor) |  | ERROR | #N/A
| Sprinklers | No | 1 | #N/A
| Note on Preliminary Result |  | 0 | 0
| Total Storage Quantity (kg) | 0
| Fire Hazard Category | N/A
| Warehouse Area (m2) | 0
| Sprinklers? | No
| Storage Type | Non-racked Storage
| Retention Volume Required m3 (with density factor) | Method not Suitable
1.1 | Area of Site which shares common drainage with Area (m2) | 0 |  | Input Required
1.11 | 1 in 10 year 24hour rainfall event for local area (m) | 0 |  | Input Required
1.12 | Rain Water (m3)1 | 0
| Fire Water Retention Required (m3) | ERROR
Note 1 | Examples of non-combustible materials include HCl, NaOH, glass container storage etc. Any non-combustible materials stored in this "assessment area" should be reviewed against their relevent Material Safety Data Sheets and confirmed as non-combustible before being included in the calculation above.
Warehouse Fire Water Retention Volume Required: A suitable firewater run-off calculation methodology for warehouse storage is a risk-based approach based on the Swiss Federation Firewater Retention Practical Guide . This method provides an opportunity for a reduction in firewater retention volume required for the site, if special fire protection measures, such as sprinklers, are provided to control and limit the fire area. This method should only be used by sites that can provide evidence of the appropriate levels of maintenance of such systems, as recommended by the applicable international or national codes or standards. The fundamental assessment factors that this method depends upon are the following; - The fire protection measures (e.g. fire detection, sprinkler type – in rack, roof level) - The fire hazard associated with the stored materials - The storage methodology (racking, piled, heights) - The density of stored materials and equipment - The assessment area size The table below outlines the preliminary retention volumes listed based on the fire compartment area, the fire hazard and the fire protection facilities. They are based on the CEA-guideline "Storage of hazardous material".
Theoretical Firewater Retention in m3
| Area of fire section | No Sprinklers |  |  |  | Sprinklers and fire detection and alarm
|  | Fire detection and Alarm |  |  |  | Stacking height < 6 m |  |  | Stacking height <12 m |  | Stacking height ≥12 m
[6 empty] | Non-racked storage | Racked storage / high bay racked storage
| In m2 | F1/F2 |  | F3/F4 | F5/F6 | F1-F6 | F1–F4 | F5/F6 | F1-F4 | F5/F6 | F1-F4 | F5/F6
|  | 1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| 50 | 50 |  | 25 | 10 | 25 | 15 | 5 | 15 | 5 | 25 | 10
| 100 | 100 |  | 50 | 20 | 45 | 30 | 10 | 35 | 15 | 50 | 20
| 150 | 180 |  | 90 | 40 | 70 | 50 | 20 | 60 | 20 | 80 | 30
| 200 | 290 |  | 140 | 60 | 90 | 60 | 20 | 90 | 40 | 120 | 50
| 250 | 390 |  | 200 | 80 | 110 | 80 | 30 | 130 | 50 | 170 | 70
| 300 | 530 |  | 270 | 110 | 160 | 110 | 50 | 210 | 90 | 260 | 110
| 400 | 790 |  | 400 | 160 | 180 | 120 | 50 | 230 | 100 | 280 | 120
| 500 | 990 |  | 500 | 200 | 210 | 140 | 60 | 250 | 110 | 300 | 130
| 600 | 1190 |  | 590 | 240 | 240 | 160 | 70 | 260 | 110 | 320 | 140
| 700 |  |  | 690 | 280 | 260 | 180 | 80 | 280 | 120 | 320 | 140
| 800 |  |  | 790 | 320 | 290 | 190 | 80 | 300 | 130 | 320 | 140
| 900 |  |  | 890 | 360 | 320 | 210 | 90 | 320 | 140 | 320 | 140
| 1000 |  |  | 990 | 400 | 340 | 230 | 100 | 320 | 140 | 320 | 140
| 1100 |  |  | 1090 | 440 | 370 | 250 | 110 | 320 | 140 | 320 | 140
| 1200 |  |  | 1190 | 480 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 1300 |  |  | 1290 | 510 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 1400 |  |  | 1390 | 550 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 1500 |  |  | 1490 | 590 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 1600 |  |  | 1580 | 630 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 1700 |  |  | 1680 | 670 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 1800 |  |  | 1780 | 710 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 1900 |  |  | 1880 | 750 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 2000 |  |  | 1980 | 790 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 2100 |  |  | 2080 | 830 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 2200 |  |  | 2180 | 870 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 2300 |  |  | 2280 | 910 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 2400 |  |  | 2380 | 950 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 2500 |  |  | 2480 | 990 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 2600 |  |  | 2580 | 1030 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 2700 |  |  | 2680 | 1070 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 2800 |  |  | 2780 | 1110 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 2900 |  |  | 2880 | 1150 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 3000 |  |  | 2960 | 1190 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 3100 |  |  | 3060 | 1230 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 3200 |  |  | 3160 | 1270 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 3300 |  |  | 3260 | 1310 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 3400 |  |  | 3360 | 1350 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 3500 |  |  | 3460 | 1390 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 3600 |  |  | 3560 | 1430 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 3700 |  |  | 3660 | 1470 | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 3800 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 3900 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 4000 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 4100 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 4200 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 4300 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 4400 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 4500 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 4600 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 4700 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 4800 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
| 4900 |  |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
Fire Water Retention Calculation

## Method 2 TF PP Area Calculation
Tank Farm and Process Plant Area
See Section 4.3 of the Guidance Report
A generalised calculation approach is required to calculate the firewater run-off retention required for a process plant or tank farm area and should take into account;
- Inventory that could be released in a credible scenario
- Fire-fighting water & foam from the following sources
• Automatic fire-fighting systems
• Fire Brigade contribution
- Extinguishing period (based on design standard or systems specifications)
- Cooling Water (based on design standard or systems specifications / discussions with local fire brigade)
- Local containment (bunding) available at area of fire only e.g. Tank Farm Bund (it is not permitted to include bunding volumes not directly affected by the fire i.e. it is not permissible to distribute contaminated firewater to other bunded areas of the site for storage
- Rainwater contribution
The estimated volumes from the above data should be quantitatively assessed to calculate the required retention volume and the following formula applied. All quantities and values used in the calculation must be set out and fully justified.
VR = VT + WE + WF + Rw – E Where, VR = Fire Water Retention Required VT = Volume of Process / Product Contribution WE = Extinguishing Medium (Water & Foam) (including Fire Brigade resources) WF = Cooling Water for Adjacent Tanks Rw = Rainwater Contribution E = Retention Volume Directly Available (i.e. capacity at area on fire only)
m3
Volume of Process / Product Contribution (VT)
Extinguishing Medium (Water & Foam including Fire Brigade resources) (WE)
Cooling Water for Adjacent Tanks (WF)
| Rainwater Contribution (Rw) - see Section 4.6.2 |  | Fire Water Retention Required (VR) | 0 | m3
Retention Volume Directly Available (i.e. capacity at area on fire only)
Fire Water Retention Calculation

## Method 3 General Calculation
General Method - Any Area
Number | Calculation Steps | Response | Comment
1.1 | Max Flow of Local Hydrants (l/min) |  | Input Required
1.2 | Fire Duration (Hours) This should be set at 6 hours unless the local fire authority has advised that a reduced time is acceptable. Note: Minimum duration is 1.5 hours |  | Input Required
1.3 | Max FW volume from hydrants during Fire Event m3 | Fire Duration Unacceptable
1.4 | Total Fire Water/Foam to be provided by Local Fire Brigade (m3) |  | Input Required
1.5 | Total Fire Water/Foam Stored on Site (m3) |  | Input Required
1.6 | Volume of Product Loss (m3) See Section 4.5 of the Guidance Document for further information |  | Input Required
1.7 | Area of Site which shares common drainage with Assessment Area (m2) |  | Input Required
1.8 | 1 in 10 year 24hour rainfall event for local area (m) |  | Input Required
1.9 | Rain Water (m3) | 0
| Fire Water Retention Required (m3) | #VALUE!
Fire Water Retention Calculation

## Information (hidden)
Likelihood of Fire: A comprehensive fire prevention assessment should ensure that all of the following measures are implemented on site: - Permanently Technically Tight Systems, High Integrity Equipment - Process Control System in Place, Automatic safety circuits for critical process steps - Ignition Source Prevention Procedures (e.g. permits, ATEX etc.) - Accredited Safety Management System - Oxygen Reduced Buildings - Regular Preventative Maintenance on Fire Detection Systems - Emergency Response Team Available on Site
Flammable Substance Thresholds (Tonnes)
| Threshold | Flammable Liquid | Flammable Solids | Flammable Gas | Combustibles
| Upper | >50 | 10 | 5 | >200
| Middle | 0.5 - 50 | 0.5 - 10 | 0.1 - 5 | 5 - 200
| Lower | 0 - 0.5 | 0 - 0.5 | 0 - 0.1 | 0 - 5
| None | 0 | 0 | 0 | 0
Hazard Potential: The ECHA Chemical Database contains information for the safe handling of hazardous substances and other chemical substances at work. Furthermore the user is offered information upon important physical and chemical properties as well as special regulations e.g. GHS classification and labelling according to CLP regulation (pictograms, H phrases, P phrases).
https://echa.europa.eu/
The GESTIS database provides WGK ratings for the majority of substances.
http://www.dguv.de/ifa/gestis/gestis-stoffdatenbank/index-2.jsp
Examples of some commonly used substance on industrial sites in large quantities;
| Substance/Material | H-Statements |  | Water Hazard Class (WGK)
| Acetone | H225 |  | 1
H319
H336
| Ammonia Solution |  |  | 2
| Calcium Cyanide |  |  | 3
| Chromic Acid |  |  | 3
| Citric Acid |  |  | 1
| Crude Oil |  |  | 3
| Diesel | H226 |  | 2
H411
| Ethanol | H225 |  | 1
H319
| HFO Components |  |  | 3
| Hydrochloric Acid |  |  | 1
| IPA |  |  | 1
| Isobutanol | H226 |  | 1
H335
| Lead Acid |  |  | 3
| Methanol |  |  | 1
| MTBE |  |  | 1
| Phenol |  |  | 2
| Sodium Hydroxide |  |  | 1
| Tetrahydrofuran (THF) |  |  | 1
| Toluene | H225 |  | 2
| Trichloroethylene (TCE) |  |  | 3
Theoretical Warehouse Fire Water Retention Volume Required: A suitable firewater run-off calculation methodology for production and warehouse storage is a risk-based approach based on the Swiss Federation Firewater Retention Practical Guide . This method provides an opportunity for a reduction in firewater retention volume required for the site, if special fire protection measures, such as sprinklers, are provided to control and limit the fire area. The use of this method should only be used by sites that can provide evidence of the appropriate levels of maintenance of such systems, as recommended by the applicable international or national codes or standards. The fundamental assessment factors that this method depends upon are the following; - The fire protection measures (e.g. fire detection, sprinkler type – in rack, roof level) - The fire hazard associated with the stored materials - The storage methodology (racking, piled, heights) - The density of stored materials and equipment - The compartment area size The table below outlines the preliminary retention volumes listed based on the fire compartment area, the fire hazard and the fire protection facilities. They are based on the CEA-guideline "Storage of hazardous material".
Theoretical Firewater Retention in m3
Area of fire section | No Sprinklers |  |  | Sprinklers and fire detection and alarm
| Fire detection and Alarm |  |  | Stacking height < 6 m |  |  | Stacking height <12 m |  | Stacking height ≥12 m
|  |  |  | Non-racked storage | Racked storage / high bay racked storage
In m2 | F1/F2 | F3/F4 | F5/F6 | F1-F6 | F1–F4 | F5/F6 | F1-F4 | F5/F6 | F1-F4 | F5/F6
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
50 | 50 | 25 | 10 | 25 | 15 | 5 | 15 | 5 | 25 | 10
100 | 100 | 50 | 20 | 45 | 30 | 10 | 35 | 15 | 50 | 20
150 | 180 | 90 | 40 | 70 | 50 | 20 | 60 | 20 | 80 | 30
200 | 290 | 140 | 60 | 90 | 60 | 20 | 90 | 40 | 120 | 50
250 | 390 | 200 | 80 | 110 | 80 | 30 | 130 | 50 | 170 | 70
300 | 530 | 270 | 110 | 160 | 110 | 50 | 210 | 90 | 260 | 110
400 | 790 | 400 | 160 | 180 | 120 | 50 | 230 | 100 | 280 | 120
500 | 990 | 500 | 200 | 210 | 140 | 60 | 250 | 110 | 300 | 130
600 | 1190 | 590 | 240 | 240 | 160 | 70 | 260 | 110 | 320 | 140
700 |  | 690 | 280 | 260 | 180 | 80 | 280 | 120 | 320 | 140
800 |  | 790 | 320 | 290 | 190 | 80 | 300 | 130 | 320 | 140
900 |  | 890 | 360 | 320 | 210 | 90 | 320 | 140 | 320 | 140
1000 |  | 990 | 400 | 340 | 230 | 100 | 320 | 140 | 320 | 140
1100 |  | 1090 | 440 | 370 | 250 | 110 | 320 | 140 | 320 | 140
1200 |  | 1190 | 480 | 390 | 260 | 110 | 320 | 140 | 320 | 140
1300 |  | 1290 | 510 | 390 | 260 | 110 | 320 | 140 | 320 | 140
1400 |  | 1390 | 550 | 390 | 260 | 110 | 320 | 140 | 320 | 140
1500 |  | 1490 | 590 | 390 | 260 | 110 | 320 | 140 | 320 | 140
1600 |  | 1580 | 630 | 390 | 260 | 110 | 320 | 140 | 320 | 140
1700 |  | 1680 | 670 | 390 | 260 | 100 | 320 | 140 | 320 | 140
1800 |  | 1780 | 710 | 390 | 260 | 110 | 320 | 140 | 320 | 140
1900 |  | 1880 | 750 | 390 | 260 | 110 | 320 | 140 | 320 | 140
2000 |  | 1980 | 790 | 390 | 260 | 110 | 320 | 140 | 320 | 140
2100 |  | 2080 | 830 | 390 | 260 | 110 | 320 | 140 | 320 | 140
2200 |  | 2180 | 870 | 390 | 260 | 110 | 320 | 140 | 320 | 140
2300 |  | 2280 | 910 | 390 | 260 | 110 | 320 | 140 | 320 | 140
2400 |  | 2380 | 950 | 390 | 260 | 110 | 320 | 140 | 320 | 140
2500 |  | 2480 | 990 | 390 | 260 | 110 | 320 | 140 | 320 | 140
2600 |  | 2580 | 1030 | 390 | 260 | 110 | 320 | 140 | 320 | 140
2700 |  | 2680 | 1070 | 390 | 260 | 110 | 320 | 140 | 320 | 140
2800 |  | 2780 | 1110 | 390 | 260 | 110 | 320 | 140 | 320 | 140
2900 |  | 2880 | 1150 | 390 | 260 | 110 | 320 | 140 | 320 | 140
3000 |  | 2960 | 1190 | 390 | 260 | 110 | 320 | 140 | 320 | 140
3100 |  | 3060 | 1230 | 390 | 260 | 110 | 320 | 140 | 320 | 140
3200 |  | 3160 | 1270 | 390 | 260 | 110 | 320 | 140 | 320 | 140
3300 |  | 3260 | 1310 | 390 | 260 | 110 | 320 | 140 | 320 | 140
3400 |  | 3360 | 1350 | 390 | 260 | 110 | 320 | 140 | 320 | 140
3500 |  | 3460 | 1390 | 390 | 260 | 110 | 320 | 140 | 320 | 140
3600 |  | 3560 | 1430 | 390 | 260 | 110 | 320 | 140 | 320 | 140
3700 |  | 3660 | 1470 | 390 | 260 | 110 | 320 | 140 | 320 | 140
3800 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
3900 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
4000 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
4100 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
4200 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
4300 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
4400 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
4500 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
4600 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
4700 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
4800 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
4900 |  |  |  | 390 | 260 | 110 | 320 | 140 | 320 | 140
Basic Fire Water Retention Calculation VR = VT + WE + WF + Rw – E Where, VR = Fire Water Retention Required VT = Volume of Primary Tank WE = Extinguishing Medium (Water & Foam) WF = Cooling Water for Adjacent Tanks Rw = Rainwater Contribution E = Retention Volume Available
For areas other than a warehouse type storage area, the retention calculation, presented in the tab "Simple Retention Calculation" can be used. Note that this is a conservative calculation that encaptures a broad range of site activities and storage types. A detailed assessment of the retention volume required for a specific area would be more accurate in providing a required volume of firewater retention. For more information, see EPA Firewater Guidance Document.
FURTHER INFORMATION